SITE INSPECTION

As you will no doubt have noticed, the regulations give little technical detail, hence it will be necessary on site to refer to the D.E.T.R. guidance document.

The checklists in this section are detailed, however, they cannot be taken as exhaustive and can, if the operative feels it prudent, be used alongside the guidance document.

INSPECTION CHECKLIST NO. 1

This checklist deals with part work, materials and fittings in contact with the water supply.

It is worthy to note that the guidance documents for the regulations concurs with the old bylaws and have banned :

- Lead and any material or substance containing lead.

- Any bituminous coatings produced from coaltar.

As you know from experience there are many installations that contain lead and lead pipework.  It would be desirable to remove these however, this action is at the clients discretion.  Careful consideration must therefore be given to jointing methods to original pipework.  Hence soldering copper pipework to lead is prohibited due to contamination by electrolytic action.  This was avoided in the past by the use of Plumbers Unions (gunmetal mechanical joints) and modern leadlock connections carry on this tradition.

# INSPECTION CHECKLIST NO. 1 MATERIALS

|  | YES | NO | NOT APPLICABLE |
| --- | --- | --- | --- |
| Does the installation contain lead pipework? |  |  |  |
| Does the installation contain bituminous coatings produced from coaltar? |  |  |  |
| Do materials carry a CE mark? |  |  |  |
| Do the materials carry a WBS teardrop mark? |  |  |  |
| Do the materials carry a WRAS approved product mark? |  |  |  |
| Do the materials carry a BSI kitemark? |  |  |  |
| Do soft solders conform to BSEN29453 for tin/copper alloys type 23 or 24? |  |  |  |
| Do soft solders conform to BSEN29453 for tin/silver alloys type 28 or 29? |  |  |  |
| Do brazing alloys contain cadmium? |  |  |  |
| Do silver solders of silver brazing metals conform to BS1845:TABLE 2 of types AG14 or AG20? |  |  |  |
| Do copper phosphorous brazing metals conform to BS1845:TABLE 3 of types CP1 – CP6? |  |  |  |
| Do jointing compounds for screw thread joints conform to BS6956:PART 5? |  |  |  |
| Do PTFE tapes (unsintered polytetrafluoroethylene) conform to BS6974 for thread applications. |  |  |  |
| Do PTFE materials conform to BS6920:PART 1? |  |  |  |

NOTES:

On new installations materials must be accepted by either a British or European standard specification.  Materials must display conformity symbols on the product or the packaging.

INSPECTION CHECKLIST

### SERVICE ENTRY TO BUILDING AND INTERNAL PIPEWORK

|  | YES | NO | NOT APPLICABLE |
| --- | --- | --- | --- |
| Does service depth conform to minimum 750mm and maximum 1350mm? |  |  |  |
| Is service entry in pipe duct? |  |  |  |
| Is service entry insulated to BS5422? |  |  |  |
| Is stop tap accessible and serviceable? |  |  |  |
| Is drain valve at lowest point? |  |  |  |
| Is pipework clip spacing to BS6700? |  |  |  |
| Are pipes spaced away from cold wall surfaces? |  |  |  |
| Are pipes in unheated spaces insulated to BS5422? |  |  |  |
| Are pipes in roof space insulated to prevent cooling or undue warming (BS5422). |  |  |  |
| If pipes pass between buildings are they insulated to BD5422? |  |  |  |